{"text_format":"1","workbook":"xlsx","n_sheets":2,"sheets":["ＤＺ特性図","計算"],"not_rendered":{"charts":0,"images":10,"macros":1,"external_links":0,"defined_names":1,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"ＤＺ特性図","index":0,"n_rows":16,"n_cols":10,"rows_kept":16,"cut":false,"hidden":false,"merged":[]}
[null," ＤＺＲｙ特性図",null,"２φＳ"]
[null,null,null,"jX ",null,null,null,"Ｒ","ｊＸ"]
[null,null,null,null,null,null,"電源  Ｚ",{"$f":"計算!$C$4","v":0.5},{"$f":"計算!$D$4","v":2.5},"Ω"]
[null,null,null,"30",null,null,"線路　Ｚ",{"$f":"計算!$C$5","v":0.5},{"$f":"計算!$D$5","v":2.5},"Ω"]
[null,null,null,null,null,null,"整定値１段",null,{"$f":"計算!$C$23","v":2.145},"Ω"]
[null,null,null,null,null,null,"整定値２段",null,{"$f":"計算!$C$24","v":5.2},"Ω"]
[null,null,null,null,null,null,"整定値３段",null,{"$f":"計算!$C$25","v":31.25},"Ω"]
[null,null,null,null,null,null,"故障点抵抗",null,{"$f":"計算!$C$13","v":0},"Ω"]
[null,null,null,null,null,null,"故障地点（変電所から）",null,{"$f":"計算!$C$14","v":100},"％"]
[null,null,null,null,null,null,"Ryの見るｚ",0.50000000025000002,2.5000000006,"Ω"]
[null,null,null,null,null,null,"〃（進相）",9.1602540422513101,0.76794919129907169,"Ω"]
[null,null,null,null,null,null,"〃（遅相）",-8.1602540417513101,4.2320508099009286,"Ω"]
[]
[]
[null,null,null,null,null,null,null,"R"]
[null,null,null,null,null,null,"30","（Ω）"]

{"sheet":"計算","index":1,"n_rows":25,"n_cols":4,"rows_kept":25,"cut":false,"hidden":false,"merged":[]}
[]
[]
[null,null,"ｒ（Ω）","ｘ（Ω）"]
["正相分","電源Ｚ",0.5,2.5]
[null,"線路Ｚ",0.5,2.5]
[null,"線路Ｃ",null,9999999999]
[]
["零相分","NGR値",300]
[null,"線路Ｃ",9999999999]
[]
[]
["線間電圧",null,6600]
["故障点抵抗（Ω）",null,0]
["故障地点（％）",null,100]
[]
[]
[]
[]
[]
[]
[]
[null," ＤＺ整定値（Ω）"]
[null,"DZ-1",2.145]
[null,"DZ-2",5.2]
[null,"DZ-D",31.25]